| HSSEQ-40 |  | Form No.: HSSEQ-40 |
| --- | --- | --- |
|  |  | Revision: 01 Date: 15 Oct 2024 |
|  | Safety Equipment & Load Line Survey Maintenance Schedules | Issued by: DPA Approved by: MD |
|  |  | Page: 1 of 82 |

Safety Equipment &

Load Line Survey

Maintenance Schedules

Vessel

Contents

- Contents	Page 03

- Master’s Monthly Inspection	Page 04

- Instructions	Page 05

- LSA & FFA Items – Certificate Expiration Dates	Pages 06 ~ 08

- Weekly Requirements	Pages 09 ~ 21

- Monthly Requirements	Pages 22 ~ 39

- Quarterly Requirements	Pages 40 ~ 41

- Annual and Other Periodic Requirements	Pages 42 ~ 60

- Loadline Survey	Pages 61 ~ 66

- LSA/FFA/Loadline maintenance records	Pages 67 ~ 78

- Drill Records	Pages 79

- Appendix 1 - Fire Extinguishers Maintenence - General notes	Pages 80 ~ 81

- Appendix 2 - List of IMO circulars related to LSA/FFA and Drill requirements	Page 82

Master’s Monthly Inspection

This booklet has been inspected and the maintenance of all equipment and all of the drill requirements have been found correctly completed and kept up to date.

| Year: | Master’s Name | Signature |
| --- | --- | --- |
| January |  |  |
| February |  |  |
| March |  |  |
| April |  |  |
| May |  |  |
| June |  |  |
| July |  |  |
| August |  |  |
| September |  |  |
| October |  |  |
| November |  |  |
| December |  |  |

Instructions

The purpose of this book is to:

  - Provide a combined record of scheduled maintenance and testing of lifesaving and fire-fighting equipment in accordance with SOLAS regulations that will ensure that equipment onboard is always fit and ready for use

  - Provide a maintenance schedule for Loadline survey items

  - Provide records of all emergency drills and training

Equipment is to be tested as required by the instructions given in the manufacturer’s user manual provided onboard.

After satisfactory inspection and routine maintenance of each piece of equipment listed then the item is to be checked off. When the section or page has been completed, then the section is to be dated and initialled.

Should any (planned or unplanned) maintenance or servicing be necessary, then this is to be entered into the “Maintenance Carried Out” sections of this book or recorded in the Planned Maintenance System records. In regard to this, all items found to be deficient are to be repaired or replaced as soon as possible.

Chief Officer is overall responsible for maintenance, inspection and verification for the state of readiness. Maintenance procedures and Inspections must be performed by a competent officer.

Certain maintenance procedures & inspections indicated herein will be required to be carried out by persons specially trained in the maintenance of such systems.

The Chief Officer shall advise the Master immediately of any identified deficiencies and the actions taken or the actions required to rectify the problem.

The Master shall inspect and sight this book monthly. He must ensure that entries are in INK and not pencil.

When any equipment is undergoing repair, the Master shall ensure that safety is not diminished by ensuring alternate arrangements are in place, such as additional equipment or shore support.

The officer-in-charge of the maintenance of the LSA/FFA/Load line equipment to ensure below general safety precautions:

- Ensure that the tasks are discussed in the daily safety meeting.

- Where necessary, prepare a detailed risk assessment and/or comply with the permit to work system requirements.

- Consider the weather conditions before planning any task.

- The shipboard management to ensure adequate supervision when the officer in charge of maintenance has inadequate experience.

- Ensure PPE compliance.

- Establish communication and ensure its effectiveness at timely intervals.

- Ensure compliance with vessel-specific and maker’s instructions.

- Additional precautions for Lifeboat related tasks:

  - Ventilate the lifeboat for at least 10 minutes by opening the main entrance door before entering

  - It is recommended to carry a personal gas detector

  - Ensure adequate maintenance of the lifeboat batteries and associated fittings

- Filling of Breathing Apparatus bottles and lifeboat air bottles

  - Trained and experienced officer to conduct the task

Note:

Flag state requirements to be followed if more stringent than the guidelines mentioned in this booklet.

Depressurize the hoses after charging lifeboat bottles/SCBA air bottles

# LSA & FFA Items – Certificate Expiration Dates

| Certificate | Issued | Expires | Remarks |
| --- | --- | --- | --- |
| Safety equipment Certificate. |  |  |  |
| Liferaft (P) Certificate. |  |  | Annual servicing. |
| Liferaft (P) Certificate. |  |  | Annual servicing. |
| Liferaft (S) Certificate. |  |  | Annual servicing. |
| Liferaft (S) Certificate. |  |  | Annual servicing. |
| Liferaft (Fwd) Certificate. |  |  | Annual servicing. |
| Inflatable lifejacket / life vest Inspection Certificate (as applicable) |  |  | Annual servicing required. |
| HRU Certificate (Non-Disposal type) |  |  | Annual servicing required. |
| EPIRB Certificate. |  |  | Battery expiry date: |
| SART Certificate. |  |  | Battery expiry date: |
| Lifeboat first aid kits Certificate. |  |  |  |
| First aid kits Certificate. |  |  |  |
| Portable fire extinguishers Certificate. |  |  | Annual Inspection and Service as per Manufacturer’s Instructions. |
| BA Compressor delivery air quality Certificate. |  |  | Annually. |
| Foam fire-extinguishing systems sample test Certificate. |  |  | Annually. |
| EEBD Certificate. |  |  | Annual Inspection as per Manufacturer’s Instructions |
| VDR test Certificate. |  |  | Annually. |
| Portable Foam Applicators sample test Certificate |  |  | Annually. |
| Chemical Suits pressure test Certificate (only in case of gas tight chemical suits) |  |  | Annually. |
| Fixed Dry Chemical Powder Systems moisture content test Certificate |  |  | Two Yearly. |
| Immersion suit and anti-exposure suit seams and closures test Certificate |  |  | Every 3 years for suits < 10 years old Annual for suits> 10 years old |
| Medical O2 cylinder Inspection Certificate (content checked and changed as required) |  |  | Every 3 years or as per manufacturer’s instruction whichever occurs sooner |
| SCBA cylinder (composite material) Hydrostatic test Certificate **Used for cargo operation – dedicated for gas / chemical carriers (as applicable) |  |  | Every 3 years or as per manufacturer’s instruction whichever sooner |
| SCBA cylinder (all steel) Hydrostatic Test Certificate |  |  | Five Yearly. |
| Foam fire-extinguishing systems proportioners test Certificate |  |  | Five Yearly. |
| EEBD Hydrostatic Test Certificate. |  |  | Five Yearly. |

* Flag state requirements shall be followed if more stringent.

* Ensure flag state guidance and approval obtained whenever there is a plan to harmonize annual service of LSA/FFA item with Class Annual Survey which falls within the window period of +/- 3 months.

# LSA & FFA Items – Certificate Expiration Dates

| Certificate | Issued | Expires | Remarks |
| --- | --- | --- | --- |
| Lifeboat Air Bottles Hydrostatic Test Certificate. |  |  | Five Yearly. |
| Medical Air / Oxygen Bottles Hydrostatic Test Certificate |  |  | Every 5 years or as per manufacturer’s instruction whichever occurs sooner |
| Fixed CO2 Fire-Extinguishing Systems Hydrostatic Test Certificate |  |  | Ten Yearly. |
| Fixed gas fire-extinguishing systems (other than CO2) Hydrostatic Test Certificate |  |  | Ten Yearly. |
| Water mist, water spray and sprinkler systems hydrostatic test of gas and water pressure cylinders. |  |  | Ten Yearly. |
| Portable and Wheeled Extinguisher Hydrostatic Test Certificate. |  |  | Ten Yearly. |
| Fixed dry chemical powder systems Hydrostatic Test Certificate of all powder containments vessels. |  |  | Ten Yearly. |
| Smoke/light for bridge lifebuoy (p) |  |  | Bridge |
| Smoke/light for bridge lifebuoy (s) |  |  | Bridge |
| 12 Rocket flares. |  |  | Bridge |
| 4 Line throwing appliances. |  |  | Bridge |
| 3 Spare portable VHF radio batteries. |  |  | (3 x Lithium batteries) |
| First aid kit #1 medicines. |  |  | Location: |
| First aid kit #2 medicines. |  |  | Location: |
| First aid kit #3 medicines. |  |  | Location: |
| First aid kit #4 medicines. |  |  | Location: |
| 2 Lifeboat smoke floats (Boat #1). |  |  | Lifeboat #1 |
| 6 Lifeboat hand flares (Boat #1). |  |  |  |
| 4 Lifeboat parachute flares (Boat #1). |  |  |  |
| Lifeboat rations (Boat #1). |  |  |  |
| Lifeboat #1 drinking water. |  |  |  |
| Lifeboat #1 torch batteries. |  |  |  Annual change |
| Wire Falls – Boat #1 Date of Renewal |  |  |  To be renewed at every 2.5 years |
| 2 Lifeboat smoke floats (Boat #2). |  |  | Lifeboat #2 |
| 6 Lifeboat hand flares (Boat #2). |  |  |  |
| 4 Lifeboat parachute flares (Boat #2). |  |  |  |
| Lifeboat rations (Boat #2). |  |  |  |
| Lifeboat # 2 drinking water. |  |  |  |
| Lifeboat #2 torch batteries. |  |  |  Annual change |

* Flag state requirements shall be followed if more stringent.

* Ensure flag state guidance and approval obt2ained whenever there is a plan to harmonize annual service of LSA/FFA item with Class Annual Survey which falls within the window period of +/- 3 months.

# LSA & FFA Items – Certificate Expiration Dates

| Certificate | Issued | Expires | Remarks |
| --- | --- | --- | --- |
| Wire Falls – Boat #2 Date of Renewal |  |  |  To be renewed at every 2.5 years |
| Small batteries with no shelf life or expiry date marked |  |  | Annual change |
| Dynamic winch brake test |  |  | Annual |
| Lifeboat Davit |  |  | See Appendices |

* Flag state requirements shall be followed if more stringent.

* Ensure flag state guidance and approval obtained whenever there is a plan to harmonize annual service of LSA/FFA item with Class Annual Survey which falls within the window period of +/- 3 months.

# Weekly Requirements

| Week No → |  | 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12 | 13 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item | Check Box |  |  |  |  |  |  |  |  |  |  |  |  |  |
| All survival craft & rescue boats/fast rescue boats launching appliances are to be visually inspected to ensure that the equipment is operationally ready for immediate use. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Lifeboat & rescue boat/fast rescue boat engine/s are to be operated for a minimum of three (3) minutes with gears being engaged in both forward and reverse. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test of General Emergency Alarm. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test of all Other General Alarms and PA System. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Check & confirm all SCBA, EEBD, ELSA & lifeboat air bottles are not leaking & are fully charged with compressed air ready for use. Confirm from gauges equipment are in correct pressure range. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify all fire detection and fire alarm control panel indicators are functional by operating the lamp / indicator test switch. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify all fixed fire-extinguishing system control panel indicators of the fixed gas fire-extinguishing systems (other than CO2) are functional by operating the lamp / indicator test switch, if applicable. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify all control / section valves of the fixed gas fire- extinguishing systems (other than CO2) are in the correct position. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify all fire door control panel indicators, if provided, are functional by operating the lamp / indicator switch. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify Low-location lighting systems are functional by switching off normal lighting in selected locations. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify all control panel indicators and alarms of water mist, water spray and sprinkler systems are functional. The system is on auto mode for immidiate operation. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Visually inspect pump unit and fittings of water mist, water spray and sprinkler systems as applicable. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Check the pump unit supply valve of water mist, water spray and sprinkler systems are in correct position to ensure automatic operation. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify all portable LSA/FFA appliances are at the designated location as per the plan. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

* Lifeboats (including free-fall lifeboats), rescue boats and fast rescue boats - Weekly and monthly inspections shall be conducted by authorized service providers, or by shipboard personnel under the direction of a senior ship’s officer in accordance with the maintenance manual(s).

# Weekly Requirements

| Week No → |  |  | 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12 | 13 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. 1 Lifeboat |  | Check Box |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Releasing Gear and Hook | The condition of releasing hook including associated hook fittings such as safety latch /safety device fitted to prevent accidental slippage of block link. Safety latch mechanism to be inspected for any deformation or damage that may result in accidental slippage of falls block from hook. Ensure moving parts are NOT painted and only lubricated for free movement |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | On-load release Gear to be properly/ completely reset |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Attachment for the Boat | Drain Valve |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Rudder and Tiller |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Handhold or Bouyant Lifeline outside of Hull |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Hand-hold on underside of Hull |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Watertight Locker or Compartments |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Painter and Painter securing device |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Arrangement for sitting and securing antenna |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Skates and Fender fitted with Lifeboat |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Flashed manually controlled Lamp (Canopy Light) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Illumination Light |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Launching Applicances | Boat to be moved from stowed position for confirming operation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Condition of Boat Davit/Launching Appliances |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Life Boat Engine | Test run for total more than 3 minutes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Checking condition of gear box and gear box train |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Lashings | Verify all lashing and securing arrangement are properly rigged and tightened as applicable to the type of the boat. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Checking Officers Confirmation. |  | Initials/Date |  |  |  |  |  |  |  |  |  |  |  |  |  |

* Lifeboats (including free-fall lifeboats), rescue boats and fast rescue boats - Weekly and monthly inspections shall be conducted by authorized service providers, or by shipboard personnel under the direction of a senior ship’s officer in accordance with the maintenance manual(s).

# Weekly Requirements

| Week No → |  |  |  | 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12 | 13 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. 2 Lifeboat |  |  | Check Box |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Releasing Gear and Hook | The condition of releasing hook including associated hook fittings such as safety latch /safety device fitted to prevent accidental slippage of block link. Safety latch mechanism to be inspected for any deformation or damage that may result in accidental slippage of falls block from hook. Ensure moving parts are NOT painted and only lubricated for free movement |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | On-load release Gear to be properly/ completely reset |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Attachment for the Boat | Drain Valve |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Rudder and Tiller |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Handhold or Bouyant Lifeline outside of Hull |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Hand-hold on underside of Hull |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Watertight Locker or Compartments |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Painter and Painter securing device |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Arrangement for sitting and securing antenna |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Skates and Fender fitted with Lifeboat |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Flashed manually controlled Lamp (Canopy Light) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Illumination Light |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Launching Applicances | Boat to be moved from stowed position for confirming operation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Condition of Boat Davit/Launching Appliances |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Life Boat Engine | Test run for total more than 3 minutes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Checking condition of gear box and gear box train |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Lashings | Verify all lashing and securing arrangement are properly rigged and tightened as applicable to the type of the boat. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| No. 1 Liferaft | Location ( | ) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| No. 2 Liferaft | Location ( | ) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| No. 3 Liferaft | Location ( | ) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| No. 4 Liferaft | Location ( | ) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| No. 5 Liferaft | Location ( | ) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| No. 6 Liferaft | Location ( | ) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Checking Officers Confirmation. |  |  | Initials/Date |  |  |  |  |  |  |  |  |  |  |  |  |  |

* Lifeboats (including free-fall lifeboats), rescue boats and fast rescue boats - Weekly and monthly inspections shall be conducted by authorized service providers, or by shipboard personnel under the direction of a senior ship’s officer in accordance with the maintenance manual(s).

# Weekly Requirements

| Week No → |  | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item | Check Box |  |  |  |  |  |  |  |  |  |  |  |  |  |
| All survival craft & rescue boats/fast rescue boats launching appliances are to be visually inspected to ensure that the equipment is operationally ready for immediate use. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Lifeboat & rescue boat/fast rescue boat engine/s are to be operated for a minimum of three (3) minutes with gears being engaged in both forward and reverse. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test of General Emergency Alarm. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test of all Other General Alarms and PA System. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Check & confirm all SCBA, EEBD, ELSA & lifeboat air bottles are not leaking & are fully charged with compressed air ready for use. Confirm from gauges equipment are in correct pressure range. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify all fire detection and fire alarm control panel indicators are functional by operating the lamp / indicator test switch. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify all fixed fire-extinguishing system control panel indicators of the fixed gas fire-extinguishing systems (other than CO2) are functional by operating the lamp / indicator test switch, if applicable. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify all control / section valves of the fixed gas fire- extinguishing systems (other than CO2) are in the correct position. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify all fire door control panel indicators, if provided, are functional by operating the lamp / indicator switch. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify Low-location lighting systems are functional by switching off normal lighting in selected locations. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify all control panel indicators and alarms of water mist, water spray and sprinkler systems are functional. The system is on auto mode for immidiate operation. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Visually inspect pump unit and fittings of water mist, water spray and sprinkler systems as applicable. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Check the pump unit supply valve of water mist, water spray and sprinkler systems are in correct position to ensure automatic operation. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify all portable LSA/FFA appliances are at the designated location as per the plan. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

* Lifeboats (including free-fall lifeboats), rescue boats and fast rescue boats - Weekly and monthly inspections shall be conducted by authorized service providers, or by shipboard personnel under the direction of a senior ship’s officer in accordance with the maintenance manual(s).

# Weekly Requirements

| Week No → |  |  | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. 1 Lifeboat |  | Check Box |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Releasing Gear and Hook | The condition of releasing hook including associated hook fittings such as safety latch /safety device fitted to prevent accidental slippage of block link. Safety latch mechanism to be inspected for any deformation or damage that may result in accidental slippage of falls block from hook. Ensure moving parts are NOT painted and only lubricated for free movement |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | On-load release Gear to be properly/ completely reset |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Attachment for the Boat | Drain Valve |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Rudder and Tiller |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Handhold or Bouyant Lifeline outside of Hull |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Hand-hold on underside of Hull |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Watertight Locker or Compartments |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Painter and Painter securing device |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Arrangement for sitting and securing antenna |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Skates and Fender fitted with Lifeboat |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Flashed manually controlled Lamp (Canopy Light) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Illumination Light |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Launching Applicances | Boat to be moved from stowed position for confirming operation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Condition of Boat Davit/Launching Appliances |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Life Boat Engine | Test run for total more than 3 minutes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Checking condition of gear box and gear box train |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Lashings | Verify all lashing and securing arrangement are properly rigged and tightened as applicable to the type of the boat. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Checking Officers Confirmation. |  | Initials/Date |  |  |  |  |  |  |  |  |  |  |  |  |  |

* Lifeboats (including free-fall lifeboats), rescue boats and fast rescue boats - Weekly and monthly inspections shall be conducted by authorized service providers, or by shipboard personnel under the direction of a senior ship’s officer in accordance with the maintenance manual(s).

# Weekly Requirements

| Week No → |  |  | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. 2 Lifeboat |  | Check Box |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Releasing Gear and Hook | The condition of releasing hook including associated hook fittings such as safety latch /safety device fitted to prevent accidental slippage of block link. Safety latch mechanism to be inspected for any deformation or damage that may result in accidental slippage of falls block from hook. Ensure moving parts are NOT painted and only lubricated for free movement |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | On-load release Gear to be properly/ completely reset |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Attachment for the Boat | Drain Valve |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Rudder and Tiller |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Handhold or Bouyant Lifeline outside of Hull |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Hand-hold on underside of Hull |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Watertight Locker or Compartments |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Painter and Painter securing device |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Arrangement for sitting and securing antenna |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Skates and Fender fitted with Lifeboat |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Flashed manually controlled Lamp (Canopy Light) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Illumination Light |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Launching Applicances | Boat to be moved from stowed position for confirming operation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Condition of Boat Davit/Launching Appliances |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Life Boat Engine | Test run for total more than 3 minutes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Checking condition of gear box and gear box train |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Lashings | Verify all lashing and securing arrangement are properly rigged and tightened as applicable to the type of the boat. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| No. 1 Liferaft | Location ( ) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| No. 2 Liferaft | Location ( ) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| No. 3 Liferaft | Location ( ) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| No. 4 Liferaft | Location ( ) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| No. 5 Liferaft | Location ( ) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| No. 6 Liferaft | Location ( ) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Checking Officers Confirmation. |  | Initials/Date |  |  |  |  |  |  |  |  |  |  |  |  |  |

* Lifeboats (including free-fall lifeboats), rescue boats and fast rescue boats - Weekly and monthly inspections shall be conducted by authorized service providers, or by shipboard personnel under the direction of a senior ship’s officer in accordance with the maintenance manual(s).

# Weekly Requirements

| Week No → |  | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item | Check Box |  |  |  |  |  |  |  |  |  |  |  |  |  |
| All survival craft & rescue boats/fast rescue boats launching appliances are to be visually inspected to ensure that the equipment is operationally ready for immediate use. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Lifeboat & rescue boat/fast rescue boat engine/s are to be operated for a minimum of three (3) minutes with gears being engaged in both forward and reverse. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test of General Emergency Alarm. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test of all Other General Alarms and PA System. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Check & confirm all SCBA, EEBD, ELSA & lifeboat air bottles are not leaking & are fully charged with compressed air ready for use. Confirm from gauges equipment are in correct pressure range. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify all fire detection and fire alarm control panel indicators are functional by operating the lamp / indicator test switch. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify all fixed fire-extinguishing system control panel indicators of the fixed gas fire-extinguishing systems (other than CO2) are functional by operating the lamp / indicator test switch, if applicable. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify all control / section valves of the fixed gas fire- extinguishing systems (other than CO2) are in the correct position. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify all fire door control panel indicators, if provided, are functional by operating the lamp / indicator switch. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify Low-location lighting systems are functional by switching off normal lighting in selected locations. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify all control panel indicators and alarms of water mist, water spray and sprinkler systems are functional. The system is on auto mode for immidiate operation. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Visually inspect pump unit and fittings of water mist, water spray and sprinkler systems as applicable. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Check the pump unit supply valve of water mist, water spray and sprinkler systems are in correct position to ensure automatic operation. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify all portable LSA/FFA appliances are at the designated location as per the plan. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

* Lifeboats (including free-fall lifeboats), rescue boats and fast rescue boats - Weekly and monthly inspections shall be conducted by authorized service providers, or by shipboard personnel under the direction of a senior ship’s officer in accordance with the maintenance manual(s).

# Weekly Requirements

| Week No → |  |  | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. 1 Lifeboat |  | Check Box |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Releasing Gear and Hook | The condition of releasing hook including associated hook fittings such as safety latch /safety device fitted to prevent accidental slippage of block link. Safety latch mechanism to be inspected for any deformation or damage that may result in accidental slippage of falls block from hook. Ensure moving parts are NOT painted and only lubricated for free movement |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | On-load release Gear to be properly/ completely reset |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Attachment for the Boat | Drain Valve |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Rudder and Tiller |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Handhold or Bouyant Lifeline outside of Hull |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Hand-hold on underside of Hull |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Watertight Locker or Compartments |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Painter and Painter securing device |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Arrangement for sitting and securing antenna |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Skates and Fender fitted with Lifeboat |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Flashed manually controlled Lamp (Canopy Light) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Illumination Light |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Launching Applicances | Boat to be moved from stowed position for confirming operation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Condition of Boat Davit/Launching Appliances |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Life Boat Engine | Test run for total more than 3 minutes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Checking condition of gear box and gear box train |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Lashings | Verify all lashing and securing arrangement are properly rigged and tightened as applicable to the type of the boat. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Checking Officers Confirmation. |  | Initials/Date |  |  |  |  |  |  |  |  |  |  |  |  |  |

* Lifeboats (including free-fall lifeboats), rescue boats and fast rescue boats - Weekly and monthly inspections shall be conducted by authorized service providers, or by shipboard personnel under the direction of a senior ship’s officer in accordance with the maintenance manual(s).

# Weekly Requirements

| Week No → |  |  | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. 2 Lifeboat |  | Check Box |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Releasing Gear and Hook | The condition of releasing hook including associated hook fittings such as safety latch /safety device fitted to prevent accidental slippage of block link. Safety latch mechanism to be inspected for any deformation or damage that may result in accidental slippage of falls block from hook. Ensure moving parts are NOT painted and only lubricated for free movement |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | On-load release Gear to be properly/ completely reset |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Attachment for the Boat | Drain Valve |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Rudder and Tiller |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Handhold or Bouyant Lifeline outside of Hull |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Hand-hold on underside of Hull |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Watertight Locker or Compartments |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Painter and Painter securing device |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Arrangement for sitting and securing antenna |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Skates and Fender fitted with Lifeboat |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Flashed manually controlled Lamp (Canopy Light) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Illumination Light |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Launching Applicances | Boat to be moved from stowed position for confirming operation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Condition of Boat Davit/Launching Appliances |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Life Boat Engine | Test run for total more than 3 minutes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Checking condition of gear box and gear box train |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Lashings | Verify all lashing and securing arrangement are properly rigged and tightened as applicable to the type of the boat. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| No. 1 Liferaft | Location ( ) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| No. 2 Liferaft | Location ( ) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| No. 3 Liferaft | Location ( ) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| No. 4 Liferaft | Location ( ) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| No. 5 Liferaft | Location ( ) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| No. 6 Liferaft | Location ( ) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Checking Officers Confirmation. |  | Initials/Date |  |  |  |  |  |  |  |  |  |  |  |  |  |

* Lifeboats (including free-fall lifeboats), rescue boats and fast rescue boats - Weekly and monthly inspections shall be conducted by authorized service providers, or by shipboard personnel under the direction of a senior ship’s officer in accordance with the maintenance manual(s).

# Weekly Requirements

| Week No → |  | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item | Check Box |  |  |  |  |  |  |  |  |  |  |  |  |  |
| All survival craft & rescue boats/fast rescue boats launching appliances are to be visually inspected to ensure that the equipment is operationally ready for immediate use. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Lifeboat & rescue boat/fast rescue boat engine/s are to be operated for a minimum of three (3) minutes with gears being engaged in both forward and reverse. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test of General Emergency Alarm. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test of all Other General Alarms and PA System. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Check & confirm all SCBA, EEBD, ELSA & lifeboat air bottles are not leaking & are fully charged with compressed air ready for use. Confirm from gauges equipment are in correct pressure range. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify all fire detection and fire alarm control panel indicators are functional by operating the lamp / indicator test switch. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify all fixed fire-extinguishing system control panel indicators of the fixed gas fire-extinguishing systems (other than CO2) are functional by operating the lamp / indicator test switch, if applicable. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify all control / section valves of the fixed gas fire- extinguishing systems (other than CO2) are in the correct position. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify all fire door control panel indicators, if provided, are functional by operating the lamp / indicator switch. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify Low-location lighting systems are functional by switching off normal lighting in selected locations. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify all control panel indicators and alarms of water mist, water spray and sprinkler systems are functional. The system is on auto mode for immidiate operation. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Visually inspect pump unit and fittings of water mist, water spray and sprinkler systems as applicable. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Check the pump unit supply valve of water mist, water spray and sprinkler systems are in correct position to ensure automatic operation. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify all portable LSA/FFA appliances are at the designated location as per the plan. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

* Lifeboats (including free-fall lifeboats), rescue boats and fast rescue boats - Weekly and monthly inspections shall be conducted by authorized service providers, or by shipboard personnel under the direction of a senior ship’s officer in accordance with the maintenance manual(s).

# Weekly Requirements

| Week No → |  |  | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. 1 Lifeboat |  | Check Box |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Releasing Gear and Hook | The condition of releasing hook including associated hook fittings such as safety latch /safety device fitted to prevent accidental slippage of block link. Safety latch mechanism to be inspected for any deformation or damage that may result in accidental slippage of falls block from hook. Ensure moving parts are NOT painted and only lubricated for free movement |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | On-load release Gear to be properly/ completely reset |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Attachment for the Boat | Drain Valve |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Rudder and Tiller |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Handhold or Bouyant Lifeline outside of Hull |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Hand-hold on underside of Hull |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Watertight Locker or Compartments |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Painter and Painter securing device |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Arrangement for sitting and securing antenna |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Skates and Fender fitted with Lifeboat |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Flashed manually controlled Lamp (Canopy Light) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Illumination Light |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Launching Applicances | Boat to be moved from stowed position for confirming operation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Condition of Boat Davit/Launching Appliances |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Life Boat Engine | Test run for total more than 3 minutes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Checking condition of gear box and gear box train |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Lashings | Verify all lashing and securing arrangement are properly rigged and tightened as applicable to the type of the boat. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Checking Officers Confirmation. |  | Initials/Date |  |  |  |  |  |  |  |  |  |  |  |  |  |

* Lifeboats (including free-fall lifeboats), rescue boats and fast rescue boats - Weekly and monthly inspections shall be conducted by authorized service providers, or by shipboard personnel under the direction of a senior ship’s officer in accordance with the maintenance manual(s).

# Weekly Requirements

| Week No → |  |  | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. 2 Lifeboat |  | Check Box |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Releasing Gear and Hook | The condition of releasing hook including associated hook fittings such as safety latch /safety device fitted to prevent accidental slippage of block link. Safety latch mechanism to be inspected for any deformation or damage that may result in accidental slippage of falls block from hook. Ensure moving parts are NOT painted and only lubricated for free movement |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | On-load release Gear to be properly/ completely reset |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Attachment for the Boat | Drain Valve |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Rudder and Tiller |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Handhold or Bouyant Lifeline outside of Hull |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Hand-hold on underside of Hull |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Watertight Locker or Compartments |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Painter and Painter securing device |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Arrangement for sitting and securing antenna |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Skates and Fender fitted with Lifeboat |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Flashed manually controlled Lamp (Canopy Light) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Illumination Light |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Launching Applicances | Boat to be moved from stowed position for confirming operation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Condition of Boat Davit/Launching Appliances |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Checking Officers Confirmation. |  | Initials/Date |  |  |  |  |  |  |  |  |  |  |  |  |  |

* Lifeboats (including free-fall lifeboats), rescue boats and fast rescue boats - Weekly and monthly inspections shall be conducted by authorized service providers, or by shipboard personnel under the direction of a senior ship’s officer in accordance with the maintenance manual(s).

# Weekly Requirements

| Week No → |  |  | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. 2 Lifeboat |  | Check Box |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Life Boat Engine | Test run for total more than 3 minutes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Checking condition of gear box and gear box train |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Lashings | Verify all lashing and securing arrangement are properly rigged and tightened as applicable to the type of the boat. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| No. 1 Liferaft | Location ( ) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| No. 2 Liferaft | Location ( ) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| No. 3 Liferaft | Location ( ) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| No. 4 Liferaft | Location ( ) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| No. 5 Liferaft | Location ( ) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| No. 6 Liferaft | Location ( ) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Checking Officers Confirmation. |  | Initials/Date |  |  |  |  |  |  |  |  |  |  |  |  |  |

* Lifeboats (including free-fall lifeboats), rescue boats and fast rescue boats - Weekly and monthly inspections shall be conducted by authorized service providers, or by shipboard personnel under the direction of a senior ship’s officer in accordance with the maintenance manual(s).

# Monthly Inspection

Lifeboat No. 1 (or Freefall Lifeboat if Carried)

| Month → |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item | Check Box |  |  |  |  |  |  |  |  |  |  |  |  |
| Name & registry marked. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Capacity, boat #, call sign marked. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Lifeboat quick release equipment. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Plug with attaching lanyard. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| External & internal fixed lights. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Small Gear/Equipment lashings. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Oars with crutches. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2 boat hooks. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1 buoyant bailer & 2 buckets. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Survival manual. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Compass with light |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Sea anchor with painter and trip line. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2 Painters (one rigged ready with quick release). |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2 Hatchets (1 fwd , 1 aft) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Freshwater (min 3 lt./person) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1 dipper and 1 graduated drinking vessel – both rustproof with lanyards. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Food rations in airtight containers. kg |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1 Whistle |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1 waterproof torch capable of morse ignalling with spare batteries and bulb. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1 daylight ignalling mirror. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Life-saving signals card (waterproof card or in waterproof container). |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4 Rocket flares, 2 smoke floats & 6 hand flares. |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Initials/Date |  |  |  |  |  |  |  |  |  |  |  |  |

* Lifeboats (including free-fall lifeboats), rescue boats and fast rescue boats - Weekly and monthly inspections shall be conducted by authorized service providers, or by shipboard personnel under the direction of a senior ship’s officer in accordance with the maintenance manual(s).

# Monthly Inspection

Lifeboat No. 1 (or Freefall Lifeboat if Carried)

| Month → |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item | Check Box |  |  |  |  |  |  |  |  |  |  |  |  |
| First aid kit in waterproof container. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Anti-seasick tablets and 1 seasick per person. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1 Jack-knife with lanyard. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3 Tin openers. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2 Thirty metre (30mtr.) buoyant ropes with quoits attached. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1 Manual pump. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1 set of fishing tackle. (line & hooks) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1 set of engine tools. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Fire extinguishers. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1 searchlight. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1 Radar reflector (a fitted transponder is acceptable). |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Diesel Fuel Tank Contents. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Compressed air (breathing air) bottle pressure. Pressure: bar Condition / Operation of Breather Valve (Pressure Valve and Vacuum Valve) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Engine start batteries. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Water spray system. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Steering tiller (separate from wheel). |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Becketed line, railings or handholds outside the boat. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Outside skates & fenders. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Portable fire extinguishers |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Waterproof lockers |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Oil lamp with oil for 12 hours burning |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Oil bag with oil for calming sea |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Initials/Date |  |  |  |  |  |  |  |  |  |  |  |  |

* Lifeboats (including free-fall lifeboats), rescue boats and fast rescue boats - Weekly and monthly inspections shall be conducted by authorized service providers, or by shipboard personnel under the direction of a senior ship’s officer in accordance with the maintenance manual(s).

# Monthly Inspection

Lifeboat No. 2 (or rescue boat/fast rescue boat if Freefall Lifeboat Carried)

| Month → |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item | Check Box |  |  |  |  |  |  |  |  |  |  |  |  |
| Name & registry marked. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Capacity, boat #, call sign marked. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Lifeboat quick release equipment. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Plug with attaching lanyard. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| External & internal fixed lights. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Small Gear/Equipment lashings. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Oars with crutches. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2 boat hooks. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1 buoyant bailer & 2 buckets. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Survival manual. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Compass with light |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Sea anchor with painter and trip line. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2 Painters (one rigged ready with quick release). |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2 Hatchets (1 fwd , 1 aft) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Freshwater (min 3 lt./person) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1 dipper and 1 graduated drinking vessel – both rustproof with lanyards. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Food rations in airtight containers. kg |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1 Whistle |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1 waterproof torch capable of morse ignalling with spare batteries and bulb. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1 daylight ignalling mirror. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Life-saving signals card (waterproof card or in waterproof container). |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4 Rocket flares, 2 smoke floats & 6 hand flares. |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Initials/Date |  |  |  |  |  |  |  |  |  |  |  |  |

Note: Required Items for rescue boat/fast rescue boat are highlighted

* Lifeboats (including free-fall lifeboats), rescue boats and fast rescue boats - Weekly and monthly inspections shall be conducted by authorized service providers, or by shipboard personnel under the direction of a senior ship’s officer in accordance with the maintenance manual(s).

# Monthly Inspection

Lifeboat No. 2 (or rescue boat/fast rescue boat if Freefall Lifeboat Carried)

| Month → |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item | Check Box |  |  |  |  |  |  |  |  |  |  |  |  |
| First aid kit in waterproof container. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Anti-seasick tablets and 1 seasick per person. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1 Jack-knife with lanyard. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3 Tin openers. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1 Buoyant line, not less than fifty (50)m in length, of sufficient strength to tow a liferaft. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1 Manual pump. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2 Thirty metre (30mtr.) buoyant ropes with quoits attached. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1 Set of fishing tackle. (line & hooks) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1 set of engine tools. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Fire extinguishers. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1 searchlight. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1 Radar reflector (a fitted transponder is acceptable). |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Diesel Fuel Tank Contents |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Compressed air (breathing air) bottle pressure. Pressure: bar Condition / Operation of Breather Valve (Pressure Valve and Vacuum Valve) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Engine start batteries. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Water spray system. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Steering tiller (separate from wheel). |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Becketed line, railings or handholds outside the boat. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Outside skates & fenders. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Portable fire extinguishers |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Waterproof lockers |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Arrangement for towing |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Oil lamp with oil for 12 hours burning |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Oil bag with oil for calming sea |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Initials/Date |  |  |  |  |  |  |  |  |  |  |  |  |

Note: Required Items for rescue boat/fast rescue boat are highlighted

* Lifeboats (including free-fall lifeboats), rescue boats and fast rescue boats - Weekly and monthly inspections shall be conducted by authorized service providers, or by shipboard personnel under the direction of a senior ship’s officer in accordance with the maintenance manual(s).

# Monthly Inspection & Testing

| Month → |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item | Check Box |  |  |  |  |  |  |  |  |  |  |  |  |
| Test the (3) portable emergency (VHF) radios and check each is fitted with a ni-cad battery and has a spare lithium battery. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test operation of EPIRB. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test operation of SART’s (2) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Check the condition of all daylight navigation signals (balls, flags, diamonds, cylinder), gong/bell and daylight ignalling devise (aldis lamp). |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Check the condition of the soundings lead line. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Check the condition of the 12 rocket flares on the bridge. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Check the condition of the 4 line throwing appliances. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test all emergency lighting & emergency batteries. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test a sample of detectors and manual call points of fixed fire detection and alarm systems so that all devices have been tested within five years. For very large systems the sample size will be determined by the administration. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test the deck foam pump. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test the fire pump. Operate all fire pumps to confirm that they continue to supply adequate pressure. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Check the condition of all pilot, lifeboat & liferaft embarkation ladders onboard and any associated securing equipment and securing points. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Check the condition of any pilot hoists onboard. |  |  |  |  |  |  |  |  |  |  |  |  |  |

* Lifeboats (including free-fall lifeboats), rescue boats and fast rescue boats - Weekly and monthly inspections shall be conducted by authorized service providers, or by shipboard personnel under the direction of a senior ship’s officer in accordance with the maintenance manual(s).

# Monthly Inspection & Testing

| Month → |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item | Check Box |  |  |  |  |  |  |  |  |  |  |  |  |
| All lifeboat davits, sheaves, fall wires, securing equipment & release gear to be checked to ensure they are free of defects, are in good condition and moving freely. To determine this the Lifeboats (Except FreeFall Lifeboats) shall be turned out from their stowed position, without any persons on board, if weather and sea conditions so allow. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Measure Vertical Clearance between the Hook and the U-bolt (should not be more than 10 mm) in the Keel Lashing (“hook/ U-Bolt”) arrangement of Free Fall lifeboat and write the results in mm. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Function of limit switch(s) shall be verified by lowering lifeboats (other than freefall) to embarkation deck and winching it to stowage position on motor. The electrical power cut off shall be tested by activation of limit switch(s). Appropriate maintenance on limit switch(s) shall be carried out using contact cleaners and moving parts lubricated as per maker’s manual to ensure free movement. Never paint moving parts / electrical contacts. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Check all lifejackets and fittings (lights, whistles, marking of ship’s name). There must be a minimum of 3 lifejacket instructional posters inside the accommodation block. |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Initials/Date |  |  |  |  |  |  |  |  |  |  |  |  |

* Lifeboats (including free-fall lifeboats), rescue boats and fast rescue boats - Weekly and monthly inspections shall be conducted by authorized service providers, or by shipboard personnel under the direction of a senior ship’s officer in accordance with the maintenance manual(s).

# Monthly Inspection & Testing

| Month → |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item | Check Box |  |  |  |  |  |  |  |  |  |  |  |  |
| Check the condition of all immersion suits and anti-exposure suits. See Appendix. Number: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Check the condition of all thermal protective aids Number: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Check the liferaft securing equipment, cradle, hydrostatic and quick release gear are rigged and ready in a good condition with the painter properly attached. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Check the forward liferaft securing equipment and cradle are rigged and ready in a good condition. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Check the condition of all lifebuoys onboard and any associated equipment (becketted ropes, retro-reflective tape, lights, marking of ship’s name & registry, smoke signals, and any quick release gear). |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Self-activating smoke floats in good order, MOB marker lights Expiry date Port Stbd Lights must be intrinsically safe for tankers |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify all control and section valves of the Foam fire-extinguishing systems are in the proper open or closed position and all pressure gauges are in the proper range. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test all deck foam monitors, valves and any associated controls. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify all portable foam applicators are in place, properly arranged, and are in proper condition. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Check the condition of all fire and foam hoses, boxes, nozzles and connections. Verify all fire hydrants, hose and nozzles are in place, properly arranged and are in serviceable condition. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify that the length of fire hoses in engine room do not exceed 15 meters |  |  |  |  |  |  |  |  |  |  |  |  |  |

Monthly Inspection & Testing

| Month → |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item | Check Box |  |  |  |  |  |  |  |  |  |  |  |  |
| Check that Isolating valves in fire and foam system lines are clearly marked are in good working order and operating freely ? |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Confirm all fire blankets are in place and in good condition. Number: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify all control, pump unit and section valves of water mist, water spray and sprinkler systems, are in the proper open or closed position. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify Sprinkler pressure tanks have correct level of water. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test automatic starting arrangements on all of water mist, water spray and sprinkler systems pumps. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify all standby pressure and air / gas pressure gauges of water mist, water spray and sprinkler systems, are within the proper pressure ranges. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test a selected sample of water mist, water spray and sprinkler system section valves for flow and proper initiation of alarms. The valves selected for testing should be chosen to ensure that all valves are tested within a one-year period. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Deck Water Spray System |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Lockers providing storage for oil pollution prevention equipment contain proper inventory and the equipment is in proper condition. |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Initials/Date |  |  |  |  |  |  |  |  |  |  |  |  |

Monthly Inspection & Testing

| Month → |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item | Check Box |  |  |  |  |  |  |  |  |  |  |  |  |
| Check that the Firemen’s outfits and breathing apparatus are in compliance with FSS code and in good order (including protective clothing, SCBA, spare bottles, safety shoes, fire axes, gloves, helmets, flashlights, safety line, 2-way portable radio telephone apparatus) and ready for immediate use? |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Confirm all compressed air bottles (SCBA, EEBD, ELSA, lifeboats) are properly connected, in good condition and remain ready for use. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Confirm all compressed medical oxygen bottles are fully charged, properly connected, in good condition and remain ready for use. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Confirm all emergency plans (muster-lists Posters) are displayed and updated on every deck. Confirm SOLAS training manual and Fire safety operational booklet are available in designated locations. They should be ship specific and updated, including latest musterlist concurrent with current crew list. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Note that 2 sets of emergency plans (with muster lists, ship’s general arrangement & fire fighting plans with an updated crew list) are to be vailable in waterproof containers outside the accommodation should be updated before arrival in every port. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify containers / cylinders of the fixed gas fire-extinguishing system (other than CO2) fitted with pressure gauges are in the proper range and the installation free from leakage. |  |  |  |  |  |  |  |  |  |  |  |  |  |

* Tanker vessels – Fireman outfit torches / flashlight must be intrinsically safe

- All ship > 500 GT: 2-way portable radio telephone apparatus must be explosion proof / intrinsically safe type

- Self-contained compressed air breathing apparatus of fire-fighter’s outfits shall be fitted with an audible alarm and a visual or other device which will alert the user before the volume of the air in the cylinder has been reduced to no less than 200 ltr.

# Monthly Inspection & Testing

| Month → |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item | Check Box |  |  |  |  |  |  |  |  |  |  |  |  |
| Check and confirm that all posted life saving & fire fighting appliance instructions posters and diagrams remain in good condition. All IMO symbols are correctly displayed and are in good condition |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify all wheeled (mobile) extinguishers are in place, properly arranged, and are in proper condition. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Lifebuoys, lights, buoyant lines, quick release mechanisms and self-activating smoke floats in good order, MOB marker lights tested as per maker’s instructions? Lights must be intrinsically safe for tankers Isolating valves in fire and foam system lines clearly marked and in good order and operating freely? Accommodation and ventilation fan emergency stops in good order and clearly marked to indicate the spaces they serve? Are all fire doors, fire dampers within accommodation in good order Are the Self door closers appropriately adjusted and the doors kept shut i.e. not made fast by rope in open position? |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify pipe and duct space cable trunking penetration is properly sealed using cement or equivalent marine gland packing for insulation and fire protection. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Check that the accommodation and ventilation fan emergency stops are in good order and clearly marked to indicate the spaces they serve? |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Check condition and markings of emergency lights(including boat deck, life rafts, fwd life raft). Ensure lights are well greased and free to operate through full limits? |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Initials/Date |  |  |  |  |  |  |  |  |  |  |  |  |

Monthly Inspection & Testing

| Month → |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item | Check Box |  |  |  |  |  |  |  |  |  |  |  |  |
| Lifeboat and liferaft area to be checked to ensure fixed lighting is properly operating and all swivels and cables are in good condition. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Fixed CO2 Fire-Extinguishing Systems |  |  |  |  |  |  |  |  |  |  |  |  |  |
| General visual inspection to be made of the overall system condition for obvious signs of damage. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verifyallstopvalvesareintheclosedposition. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify all releasing controls are in the proper position and readily accessible for immediate use. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify all discharge piping and pneumatic tubing is intact and has not been damaged. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify all high pressure cylinders are in place and properly secured. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify alarm devices are in place and do not appear damaged. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| For Bulk Carriers - All CO2 valves at the hatch coaming sides must be inspected. The valves to be operated, lubricated and maintained as required. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| For CO2 low pressure systems |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify the pressure gauge is reading in the normal range. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify the liquid level indicator is reading within the proper level. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify the manually operated storage tank main service valve is secured in the open position. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify the vapour supply line valve is secured in the open position. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Fire line inspection for leaks and corrosion joints and bottom of pipe to be visually examined. |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Initials/Date |  |  |  |  |  |  |  |  |  |  |  |  |

Monthly Inspection & Testing

| Month → |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item | Check Box |  |  |  |  |  |  |  |  |  |  |  |  |
| Safety Officer’s Rounds To inspect spaces for identification of hazards and dangerous situations and reporting to safety committee |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Chemical Suits Visual inspection of both inside and outside. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Look for surface damages on material, seams, visor, inner and outer gloves. Hold up to light and check for pinholes and cracks in the suit and gloves. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Look for changes in the material properties such as brittleness, stiffness, swelling, stickiness or other phenomena which could be evidence of chemical degradation. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Check function of zipper and zipper fitting. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Check the function of inlet valve & exhaust valves (if fitted). Make certain that they are firmly mounted and not damaged. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Check that other safety equipment (boots, gloves, goggles, fire proof line with belt, explosion proof flashlights etc) are in good condition and ready for immediate use. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Fixed dry chemical powder systems Verify all control and section valves are in the proper open or closed position, and all pressure gauges are in the proper range. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Fixed aerosol extinguishing systems systems Verify all electrical connections and / or manual operating stations are properly arranged, and are in proper condition. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verify the actuation system / control panel circuits are within manufacturer’s specifications. |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Initials/Date |  |  |  |  |  |  |  |  |  |  |  |  |

Monthly Inspection – Extinguishers

| Monthly → |  |  |  |  |
| --- | --- | --- | --- | --- |
| No. | Maker | Type | Position |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  | Initials/Date |

Monthly Inspection – Extinguishers

| No. | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Check Box |  |  |  |  |  |  |  |  |  |  |  |  |
| Initials/Date |  |  |  |  |  |  |  |  |  |  |  |  |

Monthly Inspection – Extinguishers

| Monthly → |  |  |  |  |
| --- | --- | --- | --- | --- |
| No. | Maker | Type | Position |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  | Initials/Date |

Monthly Inspection – Extinguishers

| No. | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Check Box |  |  |  |  |  |  |  |  |  |  |  |  |
| Initials/Date |  |  |  |  |  |  |  |  |  |  |  |  |

Monthly Inspection – Extinguishers

| Monthly → |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| No. | Maker | Type |  | Position |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
| Type |  |  | Number of spare Extinguisher &/or Charges |  |  |
| CO2 |  |  |  |  |  |
| Pre-mix Foam |  |  |  |  |  |
| Pressurised Foam |  |  |  |  |  |
| Pressurised Water |  |  |  |  |  |
| Soda Acid (pre-mix water) |  |  |  |  |  |
| Dry Powder |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  | Initials/Date |

Monthly Inspection – Extinguishers

| No. | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Check Box |  |  |  |  |  |  |  |  |  |  |  |  |
| Initials/Date |  |  |  |  |  |  |  |  |  |  |  |  |

Quarterly Testing & Inspections

| 3 Monthly → |  | 1st Quarter | 2nd Quarter | 3rd Quarter | 4th Quarter |
| --- | --- | --- | --- | --- | --- |
| Item | Check Box |  |  |  |  |
| Lifeboat drinking water (as applicable if drinking water is filled up in drinking water tank or jerry can without any printed expiry date). |  |  |  |  |  |
| Ensure plastic sheathing, if any, on the wires of Lifeboat, Rescue boat or Life raft lashing, is removed to facilitate inspection. |  |  |  |  |  |
| Verify the proper quantity of foam concentrate is provided in the foam fire extinguishing system storage tank. |  |  |  |  |  |
| Check the international bilge connection is in good condition with gaskets and full set of securing bolts. |  |  |  |  |  |
| The local operation of all fire doors and fire dampers is to be tested. Additionally, test all fire doors located in the main vertical zone bulkheads for local operation, if applicable. |  |  |  |  |  |
| Check that each set of safety belts for Lifeboats for a seat shall be of a colour which contrasts with the belts for seats immediately adjacent. Remove any stains and marks from the seat belts, like the grease stains. |  |  |  |  |  |
| Verify international shore connection(s) is in satisfactory condition, including condition of the flange, couplings, gasket, nuts, bolts and washers. The international shore connection should be located as per the fire plan and ready for use in an emergency. |  |  |  |  |  |
| Verify that the inventory of the equipment for helicopter ship operations is as specified in ICS Guide to Helicopter/Ship operations, and the condition is satisfactory. |  |  |  |  |  |
|  | Initials/Date |  |  |  |  |

Quarterly Testing & Inspections

| 3 Monthly → |  | 1st Quarter | 2nd Quarter | 3rd Quarter | 4th Quarter |
| --- | --- | --- | --- | --- | --- |
| Item | Check Box |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  | Initials/Date |  |  |  |  |

Annual Testing and Inspections

|  | Date Last Tested/ Checked | Date of Current Test/ Check | Name / Initials |
| --- | --- | --- | --- |
| Item | Check Box |  |  |
| Inspections in accordance with the manufacturer’s instructions and servicing of portable extinguishers. Ensure that any additional training, if required, is provided to the competent crew |  |  |  |
| Fire mains, fire pumps, hydrants, hoses and nozzles |  |  |  |
| Visually inspect all accessible components for proper condition. |  |  |  |
| Flow test all fire pumps for proper pressure and capacity. Test emergency fire pump with isolation valves closed. |  |  |  |
| Test all hydrant valves for proper operation. |  |  |  |
| Pressure test a sample of fire hoses at the maximum fire main pressure, so that all fire hoses are tested within five years. |  |  |  |
| Verify all fire pump relief valves, if provided, are properly set. |  |  |  |
| Examine all filters / strainers to verify they are free of debris and contamination. |  |  |  |
| Nozzle size / type correct, maintained and working. |  |  |  |
| The fire pipelines along with onboard are to be pressure tested and visually checked for leakage. |  |  |  |
| The fire hydrants and in-line isolating valves onboard are to be checked and tested to ensure that the seals are tight and the valves are operating freely. |  |  |  |
| All fire hoses are to be hydrostatically tested. |  |  |  |
| Fixed fire detection and fire alarm systems |  |  |  |
| Test all fire detection systems and fire detection systems used to automatically release fire-extinguishing systems for proper operation, as appropriate. |  |  |  |

Annual Testing and Inspections

|  | Date Last Tested/ Checked | Date of Current Test/ Check | Name / Initials |
| --- | --- | --- | --- |
| Item | Check Box |  |  |
| Visually inspect all accessible detectors for evidence of tampering obstruction, etc., so that all detectors are inspected within one year. |  |  |  |
| Test emergency power supply switchover. |  |  |  |
| Fixed gas fire-extinguishing systems (other than CO2) |  |  |  |
| Visually inspect all accessible components for proper condition. |  |  |  |
| Externally examine all high pressure cylinders for evidence of damage or corrosion. |  |  |  |
| Check the hydrostatic test date of all storage containers. |  |  |  |
| Functionally test all fixed system audible and visual alarms. |  |  |  |
| Verify all control / section valves are in the correct position. |  |  |  |
| Check the connections of all pilot release piping and tubing for tightness. |  |  |  |
| Examine all flexible hoses in accordance with manufacturer’s recommendations. |  |  |  |
| Test all fuel shut-off controls connected to fire-protection systems for proper operation. |  |  |  |
| The boundaries of the protected space should be visually inspected to confirm that no modifications have been made to the enclosure that have created uncloseable openings that would render the system ineffective. |  |  |  |
| If cylinders are installed inside the protected space, verify the integrity of the double release lines inside the protected space, and check low pressure or circuit integrity monitors on release cabinet, as applicable. |  |  |  |

Annual Testing and Inspections

|  | Date Last Tested/ Checked | Date of Current Test/ Check | Name / Initials |
| --- | --- | --- | --- |
| Item | Check Box |  |  |
| Foam fire-extinguishing systems |  |  |  |
| Visually inspect all accessible components for proper condition. |  |  |  |
| Functionally test all fixed system audible alarms. |  |  |  |
| Flow test all water supply and foam pumps for proper pressure and capacity, and confirm flow at the required pressure in each section (Ensure all piping is thoroughly flushed with fresh water after service). |  |  |  |
| Test all system cross connections to other sources of water supply for proper operation. |  |  |  |
| Verify all pump relief valves, if provided, are properly set. |  |  |  |
| Examine all filters/strainers to verify they are free of debris and contamination. |  |  |  |
| Verify all control / section valves are in the correct position. |  |  |  |
| Blow dry compressed air or nitrogen through the discharge piping or otherwise confirm the pipework and nozzles of high expansion foam systems are clear of any obstructions, debris and contamination. This may require the removal of nozzles, if applicable. |  |  |  |
| Take samples from all foam concentrates carried on board and subject them to the periodical control tests in MSC.1/Circ.1312, for low expansion foam, or MSC/Circ.670 for high expansion foam. See Appendix (Note: Except for non-alcohol resistant foam, the first test need not be conducted until 3 years after being supplied to the ship.). * |  |  |  |
| Test all fuel shut-off controls connected to fire-protection systems for proper operation. |  |  |  |
| The foam pipelines along with onboard are to be pressure tested and visually checked for leakage. |  |  |  |

* Testing to be carried out by specially trained personnel.

Annual Testing and Inspections

|  | Date Last Tested/ Checked | Date of Current Test/ Check | Name / Initials |
| --- | --- | --- | --- |
| Item | Check Box |  |  |
| The foam hydrants and in-line isolating valves onboard are to be checked and tested to ensure that the seals are tight and the valves are operating freely. |  |  |  |
| All foam hoses are to be hydrostatically tested. |  |  |  |
| Water mist, water spray and sprinkler systems |  |  |  |
| Verify proper operation of all water mist, water-spray and sprinkler systems using the test valves for each section. |  |  |  |
| Visually inspect all accessible components for proper condition. |  |  |  |
| Externally examine all high pressure cylinders for evidence of damage or corrosion. |  |  |  |
| Check the hydrostatic test date of all high pressure cylinders. |  |  |  |
| Functionally test all fixed system audible and visual alarms. |  |  |  |
| Flow test all pumps for proper pressure and capacity. |  |  |  |
| Test all antifreeze systems for adequate freeze protection. |  |  |  |
| Test all system cross connections to other sources of water supply for proper operation. |  |  |  |
| Verify all pump relief valves, if provided, are properly set. |  |  |  |
| Examine all filters / strainers to verify they are free of debris and contamination. |  |  |  |
| Verify all control/section valves are in the correct position. |  |  |  |
| Test emergency power supply switchover, where applicable. |  |  |  |
| Check for any changes that may affect the system such as obstructions by ventilation ducts, pipes, etc. |  |  |  |

Annual Testing and Inspections

|  | Date Last Tested/ Checked | Date of Current Test/ Check | Name / Initials |
| --- | --- | --- | --- |
| Item | Check Box |  |  |
| Blow dry compressed air or nitrogen through the discharge piping of dry pipe systems, or otherwise confirm the pipework and nozzles are clear of any obstructions. This may require the removal of nozzles, if applicable. |  |  |  |
| Visually inspect all sprinklers focusing in areas where sprinklers are subject to aggressive atmosphere (like saunas, spas, kitchen areas) and subject to physical damage (like luggage handling areas, gyms, play rooms, etc.) so that all sprinklers are inspected within one year. |  |  |  |
| Test a minimum of one section in each open head water mist system by flowing water through the nozzles. The sections tested should be chosen so that all sections are tested within a five-year period. |  |  |  |
| Test a minimum of two automatic sprinklers or automatic water mist nozzles for proper operation. |  |  |  |
| Ventilation systems and fire dampers |  |  |  |
| Test all fire dampers for remote operation. |  |  |  |
| Verify galley exhaust ducts and filters are free of grease build-up. |  |  |  |
| Test all ventilation controls interconnected with fire-protection systems for proper operation. |  |  |  |
| Fire Doors |  |  |  |
| Test all remotely controlled fire doors for proper release. |  |  |  |
| Medical O2 bottle and resuscitation equipment The entire system is to be inspected annually by a competent person in accordance with manufacturer’s instructions. |  |  |  |

* Medical O2 bottle and resuscitation equipment - The entire system is to be inspected annually by a competent person in accordance with manufacturer’s instructions and acceptable to the vessel’s classification society.

* Ensure medical oxygen space is properly ventilated, cannot be easily damaged or disturbed, protected location and not exposed to excessive heat, flames or corrosive atmosphere.

# Annual Testing and Inspections

|  | Date Last Tested/ Checked | Date of Current Test/ Check | Name / Initials |
| --- | --- | --- | --- |
| Item | Check Box |  |  |
| Breathing apparatus |  |  |  |
| Check breathing apparatus air recharging systems, if fitted, for air quality.* |  |  |  |
| Check all breathing apparatus face masks and air demand valves are in serviceable condition. |  |  |  |
| Check EEBDs according to maker’s instructions. Ensure that any additional training, if required, is provided to the competent crew |  |  |  |
| Portable foam applicators |  |  |  |
| Verify all portable foam applicators are set to the correct proportioning ratio for the foam concentrate supplied and the equipment is in proper order. |  |  |  |
| Verify all portable containers or portable tanks containing foam concentrate remain factory sealed, and the manufacturer’s recommended service life interval has not been exceeded. |  |  |  |
| Portable containers or portable tanks containing foam concentrate, excluding protein based concentrates, less than 10 years old, that remain factory sealed can normally be accepted without the periodical foam control tests required in MSC.1/Circ.1312 being carried out. Verify same if applicable.* |  |  |  |
| The foam concentrates of any non-sealed portable containers and portable tanks, and portable containers and portable tanks where production data is not documented, should be subjected to the periodical foam control tests required in MSC.1/Circ.1312 * |  |  |  |

* Testing to be carried out by specially trained personnel.

Annual Testing and Inspections

|  | Date Last Tested/ Checked | Date of Current Test/ Check | Name / Initials |
| --- | --- | --- | --- |
| Item | Check Box |  |  |
| Wheeled (mobile) fire extinguishers |  |  |  |
| Perform periodical inspections in accordance with the manufacturer’s instructions. Ensure that any additional training, if required, is provided to the competent crew |  |  |  |
| Visually inspect all accessible components for proper condition. |  |  |  |
| Check the hydrostatic test date of each cylinder. |  |  |  |
| For dry powder extinguishers, invert extinguisher to ensure powder is agitated. |  |  |  |
| Galley and deep fat cooking fire- extinguishing systems |  |  |  |
| Check galley and deep fat cooking fire- extinguishing systems in accordance with the manufacturer’s instructions. Ensure that any additional training, if required, is provided to the competent crew |  |  |  |
| Lifeboat Launching Appliances |  |  |  |
| Thorough examination at the annual surveys followed by a dynamic test of the winch brake at maximum lowering speed. Load to be applied shall be the mass of the survival craft or rescue boat/fast rescue boat without persons on board. * |  |  |  |

* Testing to be carried out by specially trained personnel.

- Lifeboats (including free-fall lifeboats), rescue boats / fast rescue boats and liferafts - Annual thorough examinations and operational tests shall be conducted by certified personnel from either the manufacturer or an authorized service provider - authorized by the flag administration (or its recognized organizations, ROs). Flag administrations (or their ROs) will issue the authorization document and ensure that information regarding authorized service providers is made available. The service provider may be the ship operator, provided they are authorized.

- In case where a manufacturer is no longer in business or no longer provides technical support, the Administration may  authorize service providers for equipment on the basis of prior authorization for the equipment and/or long-term experience and demonstrated expertise as an authorized service provider. Personnel for the work specified shall be certified by the manufacturer or authorized service provider for each make and type of the equipment to be worked on.

# Annual Testing and Inspections

|  | Date Last Tested/ Checked | Date of Current Test/ Check | Name / Initials |
| --- | --- | --- | --- |
| Item | Check Box |  |  |
| Lifeboat or rescue boat/fast rescue boat on-load release gear, including free-fall release systems |  |  |  |
| Launching appliances as well as on-load and off-load release gear for lifeboats (including primary and secondary means of launching appliances for free-fall lifeboats), rescue boats, fast rescue boats and davit-launched liferafts. Thorough examination and operational test during the annual surveys required by certified personnel from either the manufacturer or an authorized service provider. Refer to footnote* |  |  |  |
| Davit-launched liferaft automatic release hooks |  |  |  |
| Launching appliances for davit-launched liferafts. Thorough examination and operational test during the annual surveys required by certified personnel from either the manufacturer or an authorized service provider. Refer to footnote* |  |  |  |
| HRU (Non-Disposal Type) |  |  |  |
| Servicing unit in accordance with manufacturer’s recommendation *. |  |  |  |
| Inflatable lifejacket / life vest |  |  |  |
| Servicing in accordance with manufacturer’s recommendation *. |  |  |  |
| Immersion suit and anti-exposure suit (> 10 years old) |  |  |  |
| Servicing in accordance with manufacturer’s recommendation including seams and closure test *. |  |  |  |
| EPIRB |  |  |  |
| Servicing in accordance with manufacturer’s recommendation *. |  |  |  |

* Testing to be carried out by specially trained personnel.

- Lifeboats (including free-fall lifeboats), rescue boats / fast rescue boats and liferafts - Annual thorough examinations and operational tests shall be conducted by certified personnel from either the manufacturer or an authorized service provider - authorized by the flag administration (or its recognized organizations, ROs). Flag administrations (or their ROs) will issue the authorization document and ensure that information regarding authorized service providers is made available. The service provider may be the ship operator, provided they are authorized.

- In case where a manufacturer is no longer in business or no longer provides technical support, the Administration may authorize service providers for equipme2nt on the basis of prior authorization for the equipment and/or long-term experience and demonstrated expertise as an authorized service provider. Personnel for the work specified shall be certified by the manufacturer or authorized service provider for each make and type of the equipment to be worked on.

# Annual Testing and Inspections

|  | Date Last Tested/ Checked | Date of Current Test/ Check | Name / Initials |
| --- | --- | --- | --- |
| Item | Check Box |  |  |
| Fixed CO2 Fire-Extinguishing Systems |  |  |  |
| (The following minimum level of maintenance and inspections should be carried out in accordance with the system manufacturer’s instructions and safety precautions). |  |  |  |
| The boundaries of the protected space should be visually inspected to confirm that no modifications have been made to the enclosure that have created uncloseable openings that would render the system ineffective. |  |  |  |
| The manifold should be inspected to verify that all flexible discharge hoses and fittings are properly tightened. |  |  |  |
| All storage containers should be visually inspected for any signs of damage, rust or loose mounting hardware. Cylinders that are leaking, corroded, dented or bulging should be hydrostatically retested or replaced. |  |  |  |
| System piping should be visually inspected to check for damage, loose supports and corrosion. Nozzles should be inspected to ensure they have not been obstructed by the storage of spare parts or a new installation of structure or machinery. |  |  |  |
| All entrance doors to the protected space should close properly and should have warning signs, which indicate that the space is protected by a fixed carbon dioxide system and that personnel should evacuate immediately if the alarms sound. All remote releasing controls should be checked for clear operating instructions and indication as to the space served. |  |  |  |
| Chemical suits Pressure test of chemical suits as per manufacturer’s guidelines (only in case of gas tight chemical suits) Ensure that any additional training, if required, is provided to the competent crew |  |  |  |

- To be carried out by specially trained personnel.

# Annual Testing and Inspections

|  | Date Last Tested/ Checked | Date of Current Test/ Check | Name / Initials |
| --- | --- | --- | --- |
| Item | Check Box |  |  |
| Fixed dry chemical powder systems Visually inspect all accessible components for proper condition. |  |  |  |
| Verify the pressure regulators are in proper order within calibration. |  |  |  |
| Agitate the dry chemical with nitrogen in accordance with system manufacturer’s instructions. (Note: Due to the powder’s affinity for moisture, any nitrogen gas introduced for agitation must be moisture free.) * |  |  |  |
| Miscellaneous All anti-freeze systems are to be tested for proper solutions. |  |  |  |

* To be carried out by specially trained personnel.

# Two Yearly Testing and Inspections

|  | Date Last Tested/ Checked | Date of Current Test/ Check | Name / Initials |
| --- | --- | --- | --- |
| Item | Check Box |  |  |
| Fixed gas fire-extinguishing systems (other than CO2) |  |  |  |
| All high pressure extinguishing agents cylinders and pilot cylinders should be weighed or have their contents verified by other reliable means to confirm that the available charge in each is above 95 per cent of the nominal charge. Cylinders containing less than 95 per cent of the nominal charge should be refilled. * |  |  |  |
| Blow dry compressed air or nitrogen through the discharge piping or otherwise confirm the pipe work and nozzles are clear of any obstructions. This may require the removal of nozzles, if applicable. |  |  |  |
| Fixed dry chemical powder systems* Blow dry nitrogen through the discharge piping to confirm that the pipe work and nozzles are clear of any obstructions. |  |  |  |
| Operationally test local and remote controls and section valves |  |  |  |
| Verify the contents of propellent gas cylinders (including remote operating stations.) |  |  |  |
| Test a sample of dry chemical powder for moisture content. |  |  |  |
| Subject the powder containment vessel, safety valve and discharge hoses to a full working pressure test. |  |  |  |

- To be carried out by specially trained personnel.

# Three Yearly Testing and Inspections

(To be carried out by specially trained personnel)

|  | Date Last Tested/ Checked | Date of Current Test/ Check | Name / Initials |
| --- | --- | --- | --- |
| Item | Check Box |  |  |
| Medical O2 bottle |  |  |  |
| The contents of the cylinders are to be checked and changed as required per manufacturer’s requirements. |  |  |  |
| SCBA cylinder (composite material) Perform hydrostatic testing of all composite material self-contained breathing apparatus cylinders. |  |  |  |
| Immersion suit and anti-exposure suit (< 10 years old) |  |  |  |
| Servicing in accordance with manufacturer’s recommendation including seams and closure test *. |  |  |  |

Five Yearly Testing and Inspections

(To be carried out by specially trained personnel)

|  | Date Last Tested/ Checked | Date of Current Test/ Check | Name / Initials |
| --- | --- | --- | --- |
| Item | Check Box |  |  |
| Fixed CO2 Fire-Extinguishing Systems |  |  |  |
| At each intermediate, periodical or renewal survey in cargo ships, the following maintenance should be carried out (to assist in carrying out the recommended maintenance, examples of service charts are set out in the appendix). |  |  |  |
| All high pressure cylinders and pilot cylinders should be weighed or have their contents verified by other reliable means to confirm that the available charge in each is above 90% of the nominal charge. Cylinders containing less than 90% of the nominal charge should be refilled. The liquid level of low pressure storage tanks should be checked to verify that the required amount of carbon dioxide to protect the largest hazard is available. |  |  |  |
| The hydrostatic test date of all storage containers should be checked. High- pressure cylinders should be subjected to periodical tests at intervals not exceeding 10 years. At the 10-year inspection, at least 10% of the total number provided should be subjected to an internal inspection and hydrostatic test. If one or more cylinders fail, a total of 50% of the onboard cylinders should be tested. If further cylinders fail, all cylinders should be tested. Before the 20-year anniversary and every 10-year anniversary thereafter, all cylinders should be subjected to a hydrostatic test. Flexible hoses should be replaced at the intervals recommended by the manufacturer andnot exceeding every 10 years. When cylinders are removed for testing, the cylinders should be replaced such that the quantity of fire-extinguishing medium continues to satisfy the requirements of 2.2.1 of chapter 5 of the FSS Code, subject to SOLAS regulation II-2/14.2 |  |  |  |
| The discharge piping and nozzles should be tested to verify that they are not blocked. The test should be performed by isolating the discharge piping from the system and flowing dry air or nitrogen from test cylinders or suitable means through the piping. |  |  |  |

Five Yearly Testing and Inspections

(To be carried out by specially trained personnel)

|  | Date Last Tested/ Checked | Date of Current Test/ Check | Name / Initials |
| --- | --- | --- | --- |
| Item | Check Box |  |  |
| At each renewal survey in cargo ships, the following maintenance should be carried out by service technicians / specialists trained to standards accepted by the Administration. Where possible, all activating heads should be removed from the cylinder valves and tested for correct functioning by applying full working pressure through the pilot lines. In cases where this is not possible, pilot lines should be disconnected from the cylinder valves and blanked off or connected together and tested with full working pressure from the release station and checked for leakage. In both cases this should be carried out from one or more release stations when installed. If manual pull cables operate the remote release controls, they should be checked to verify the cables and corner pulleys are in good condition and freely move and do not require an excessive amount of travel to activate the system. |  |  |  |
| All cable components should be cleaned and adjusted as necessary, and the cable connectors should be properly tightened. If the remote release controls are operated by pneumatic pressure, the tubing should be checked for leakage, and the proper charge of the remote releasing station pilot gas cylinders should be verified. All controls and warning devices should function normally, and the time delay, if fitted should prevent the discharge of gas for the required time period. |  |  |  |

Five Yearly Testing and Inspections

(To be carried out by specially trained personnel)

|  | Date Last Tested/ Checked | Date of Current Test/ Check | Name / Initials |
| --- | --- | --- | --- |
| Item | Check Box |  |  |
| After completion of the work, the system should be returned to service. All releasing controls should be verified in the proper position and connected to the correct control valves. All pressure switch interlocks should be reset and returned to service. All stop valves should be in the closed position. |  |  |  |
| Fixed gas fire-extinguishing systems (including CO2 systems) |  |  |  |
| Perform internal inspection of all control valves. |  |  |  |
| Foam fire-extinguishing systems |  |  |  |
| Perform internal inspection of all control valves. |  |  |  |
| Flush all high expansion foam system piping with fresh water, drain and purge with air. |  |  |  |
| Check all nozzles to prove they are clear of debris. |  |  |  |
| Test all foam proportioners or other foam mixing devices to confirm that the mixing ratio tolerance is within +30 to –10% of the nominal mixing ratio defined by the system approval. |  |  |  |
| Water mist, water spray and sprinkler systems |  |  |  |
| Flush all ro-ro deck deluge system piping with water, drain and purge with air. |  |  |  |
| Perform internal inspection of all control / section valves. |  |  |  |

Five Yearly Testing and Inspections

(To be carried out by specially trained personnel)

|  | Date Last Tested/ Checked | Date of Current Test/Check | Name / Initials |
| --- | --- | --- | --- |
| Item | Check Box |  |  |
| Check condition of any batteries, or renew in accordance with manufacturer’srecommendations. |  |  |  |
| Breathing apparatus |  |  |  |
| Perform hydrostatic testing of all steelself-contained breathing apparatus cylinders. Aluminium and composite cylinders should be tested to the satisfaction of the Administration. |  |  |  |
| EEBD |  |  |  |
| Perform hydrostatic testing. Device should be tested in accordance with manufacturer’s recommendation. |  |  |  |
| Low-location lighting |  |  |  |
| Test the luminance of all systems inaccordance with the procedures in resolution A.752(18). |  |  |  |
| Wheeled (mobile) fire extinguishers |  |  |  |
| Visually examine at least one extinguisherof each type manufactured in the same year and kept on board. |  |  |  |
| Portable Extinguisher |  |  |  |
| At least one extinguisher of each type manufactured in the same year and keptonboard a ship to be discharged as partof a drill |  |  |  |
| Lifeboat Launching Appliances |  |  |  |
| Thorough examination at the renewal surveys followed by a dynamic test of the winch brake at maximum lowering speed. Proof load to be applied shall be 1.1 times the weight of the survival craft or rescue boat and its full complement ofpersons and equipment. |  |  |  |

Five Yearly Testing and Inspections

(To be carried out by specially trained personnel)

|  | Date Last Tested/ Checked | Date of Current Test/ Check | Name / Initials |
| --- | --- | --- | --- |
| Item | Check Box |  |  |
| Lifeboat or rescue boat/fast rescue boat on-load release gear, including free-fall release systems |  |  |  |
| Overhaul of the release gear and followed by an operational test under a load of 1.1 times the total mass of the boat when loaded with its full complement ofpersons and equipment. |  |  |  |
| Davit-launched liferaft automaticrelease hooks |  |  |  |
| Overhaul of the automatic release hooks and followed by an operational test under a load of 1.1 times the total mass of the liferaft when loaded with its full complement of persons and equipment. |  |  |  |
| Lifeboat and Medical air / oxygenbottles |  |  |  |
| Hydrostatic test of lifeboat and medical air/oxygen bottles. |  |  |  |

Ten Yearly Testing and Inspections

(To be carried out by specially trained personnel)

|  | Date Last Tested/ Checked | Date of Current Test/ Check | Name / Initials |
| --- | --- | --- | --- |
| Item | Check Box |  |  |
| Fixed gas fire-extinguishing systems (other than CO2) |  |  |  |
| Perform a hydrostatic test and internal examination of 10 per cent of the system’s extinguishing agent and pilot cylinders. If one or more cylinders fail, a total of 50 per cent of the onboard cylinders should be tested. If further cylinders fail, all cylinders should be tested. |  |  |  |
| Flexible hoses should be replaced at the intervals recommended by the manufacturer and not exceeding every 10 years. |  |  |  |
| If permitted by the Administration, visual inspection and NDT (non-destructive testing) of halon cylinders may be performed in lieu of hydrostatic testing. |  |  |  |
| Water mist, water spray and sprinkler systems |  |  |  |
| Perform a hydrostatic test and internal examination for gas and water pressure cylinders according to flag Administration guidelines or, where these do not exist, EN 1968:2002 + A1. |  |  |  |
| Wheeled (mobile) fire extinguishers |  |  |  |
| All extinguishers together with propellant cartridges should be hydrostatically tested by specially trained persons in accordance with recognized standards or the manufacturer’s instructions. |  |  |  |

Ten Yearly Testing and Inspections

(To be carried out by specially trained personnel)

|  | Date Last Tested/ Checked | Date of Current Test/ Check | Name / Initials |
| --- | --- | --- | --- |
| Item | Check Box |  |  |
| Portable Extinguisher |  |  |  |
| All extinguishers together with propellant cartridges should be hydraulically testedin accordance with the recognized standard or the manufacturer’s instruction. |  |  |  |
| Fixed dry chemical powder systems |  |  |  |
| Subject all powder containment vesselsto hydrostatic or non-destructive testing carried out by an accredited service agent. |  |  |  |
| Fixed aerosol extinguishing systems |  |  |  |
| Condensed or dispersed aerosol generators to be renewed in accordance with manufacturer’s recommendations. |  |  |  |

Loadline Survey

| 3 Monthly → |  | 1st Quarter | 2nd Quarter | 3rd Quarter | 4th Quarter |
| --- | --- | --- | --- | --- | --- |
| Item | Check Box |  |  |  |  |

| All natural vent pipes and vent heads - Thorough inspection on internal & external condition including mesh, fittings, rubber packings and non-return mechanisms like disc, float etc. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Ensure there is safe access to bow and catwalk |  |  |  |  |  |
| Check condition of all sounding pipes, covers (and quick closing appliances if fitted) |  |  |  |  |  |

|  | Inspection Interval | Date Last Tested/Checked | Date of Current Test/Check | Name / Initials |
| --- | --- | --- | --- | --- |
| Item | Check Box |  |  |  |
| Draft marks | As necessary |  |  |  |
| Inspect the vessels lifelines, railings and any other fittings that ensure secure passage along the deck for crew in bad weather to ensure they remain in good condition | 6 months |  |  |  |
| Check that guard rails, chains and wires around coamings remain in good condition | 6 months |  |  |  |
| Check the condition of hatch coaming packing, securing devices and fittings for good condition | 6 months |  |  |  |
| Check the condition and operation of valves and self closing mechanisms on vents | 6 months |  |  |  |
| Check the condition of windows, portholes, deadlights and any associated packings, hinges and fittings | 6 months |  |  |  |
| Check the condition and operation of any hold, store room, locker or void space bilge piping and any associated suction and non-return valves, reach-rods, wells/ sumps and markings | 6 months |  |  |  |
| Check that any hold, store room, lockers or void space bilge suction pumps and eductors are operating correctly | 6 months |  |  |  |
| Deadlights | 6 months |  |  |  |

Requirements for additional checks for air vents as below:

  - Verify condition after adverse weather especially when in ballast condition as the vent discs/ floats/ rubber packing can be dislodged/ damaged after the water sloshing from the vents.

  - Verify condition after ballast water exchange (when done by FLOW through) as the discs/ floats/ rubber packing can be dislodged/ damaged due to the operation.

  - Vessels having the arrangement of the spindle and the floating DISC should ensure that the SPINDLE is properly secured (not shaking/ wobbling/out of slot etc) and the disc is freely moving.

# Loadline Survey

|  | Inspection Interval | Date Last Tested/Checked | Date of Current Test/Check | Name / Initials |
| --- | --- | --- | --- | --- |
| Item | Check Box |  |  |  |
| Bulk Carriers |  |  |  |  |
| Gaskets / lips / compression bars / drainage channels Examine the non-return valves in drainage channels and that packing material is not perished or torn | 6 months |  |  |  |
| Clamping / cleatings / retaining bars Examine that the retaining bars and compression bars are not affected by excessive wastage and that cleatings ensure compression when covers are seated (special attention to cross joints). | 6 months |  |  |  |
| Stoppers / guide rails / track wheels / chain or rope pulleys Examine the maintenance of stoppers, guide rails, track wheels and chain or rope pulleys. | 6 months |  |  |  |
| Hatch covers Hatch covers with respect to corrosion, cracks or deformation. Examine residual thickness of pontoons or covers, plating and stiffening members, as deemed necessary by the surveyor. If the surveyor deems it necessary to verify the tightness of hatch covers more thoroughly than by visual examination a tightness test as required by renewal survey might be carried out. | 6 months |  |  |  |
| Hatch covers For bulk carriers and general dry cargo vessels more than 15 years of age, all hatch covers are required to be hose tested. However, equivalent testing methods may be accepted, e.g. Air test on combination carriers, or Ultrasonic test by certified body. Guidance: Nozzle diameter: Minimum 12mm. Water Pressure: Sufficient for a free height of water with stream directed upwards of min. 10m. Distance: Max. 1.5m | 6 months |  |  |  |
| Hatch coamings Examine the condition of coamings with stiffeners and connection to deck with respect to corrosion, cracks or deformation to plating and supporting members | 6 months |  |  |  |

Loadline Survey

|  | Inspection Interval | Date Last Tested/Checked | Date of Current Test/Check | Name / Initials |
| --- | --- | --- | --- | --- |
| Item | Check Box |  |  |  |
| Bulk Carriers |  |  |  |  |
| Hatch covers function tested at random Examine stowage and securing of selected hatch covers (open condition). Examine proper fit, locking and efficiency of sealings (close condition) | 6 months |  |  |  |
| Superstructures, deckhouses and companionways with their bulkheads Examine the condition of bulkheads in superstructures, deckhouses, companionways and casings with respect to corrosion, cracks and buckles | 6 months |  |  |  |
| Doors Examine the condition of plating, stiffeners, clamping devices, hinges, packings and sills. Hose test as for hatch covers if deemed necessary | 6 months |  |  |  |
| Small hatches Examine the condition of covers and coamings with stiffeners and deck connection, with respect to corrosion, cracks and deformation to plating and supporting members. Examine the condition and function of the securing devices, especially the toggles and their tongues with respect to corrosion and deformation. Hose test as for hatch covers if deemed necessary | 6 months |  |  |  |
| Engine and boiler casings with their doors, sills, skylights Examine the condition of clamping devices, hinges, packings and sills. Hose test as for hatch covers if deemed necessary | 6 months |  |  |  |

Loadline Survey

|  | Inspection Interval | Date Last Tested/Checked | Date of Current Test/Check | Name / Initials |
| --- | --- | --- | --- | --- |
| Item | Check Box |  |  |  |
| Bulk Carriers |  |  |  |  |
| Ventilators Examine the condition of coamings with stays / supports especially connection to the deck. Weathertightness of closing appliances to be examined | 6 months |  |  |  |
| Ventilators on fore deck (forward quarter length) Special attention shall be made to the deck connections and welding to the deck. The condition of each pipe shall be specially examined w.r.t. corrosion. Thickness measurements if deemed necessary. Maximum 25% diminution of DNV Rule thickness is accepted, ref. IS II-2.3 | 6 months |  |  |  |
| Air pipes Examine the condition of pipe and connection the deck. Weathertightness of closing appliances to be examined | 6 months |  |  |  |
| Airpipes on fore deck (forward quarter length) Special attention shall be made to the deck connections and welding to the deck. The condition of each pipe shall be specially examined w.r.t. corrosion. Thickness measurements if deemed necessary. Maximum 25% diminution of DNV Rule thickness is accepted, ref. IS II-2.3 | 6 months |  |  |  |
| Side scuttles and windows Examine the weathertighness of scuttles in ship sides and enclosed superstructure and for windows / scuttles in deckhouses. Hinges and toggles to be easily movable | 6 months |  |  |  |
| Deadlights Examine w.r.t. weathertightness (rubber gasket). Hinges and toggles to be esily movable. For supply vessels and standby vessels deadlights may be required at higher positions according to DNV rules 6 months | 6 months |  |  |  |

Loadline Survey

|  | Inspection Interval | Date Last Tested/Checked | Date of Current Test/Check | Name / Initials |
| --- | --- | --- | --- | --- |
| Item | Check Box |  |  |  |
| Bulk Carriers |  |  |  |  |
| Gaskets and closing devices tightness tested Tightness test as for hatch covers may be required if deemed necessary by the surveyor. (test mandatory at renewal survey) | 6 months |  |  |  |
| Bulwarks, guardrails and lifelines Examine the stanchions, stay, courses and wire / chain. If underdeck passage, check ventilation, lighting and gas, oil and weathertightness | 6 months |  |  |  |
| Safe access to bow Examine the shelters, stanchions, stays, courses and wire/chain. Where detachable stanchions with wire ropes are used, these shall be mounted up | 6 months |  |  |  |
| Freeing ports and shutters Examine the rails, bars and shutters | 6 months |  |  |  |
| Sea inlet and outlet valves, scuppers and sanitary discharge valves Examine the external condition of valves with respect to tightness, corrosion and hold down bolts | 6 months |  |  |  |
| Remote operation of valves tested and verification of “fail to safe” To be tested in operation | 6 months |  |  |  |

Annual and dry-dock check – All vessels

| Item | Check Box |  |  |  |
| --- | --- | --- | --- | --- |
| All hatches, WT doors, vents etc. are to be secured and then hose tested | Annual |  |  |  |
| Overhaul the hinges, dogs and packing on watertight doors | Annual |  |  |  |
| ACheck the hinges, locks and fittings on wooden and other non-watertight weather doors | Annual |  |  |  |

Loadline Survey

|  | Inspection Interval | Date Last Tested/Checked | Date of Current Test/Check | Name / Initials |
| --- | --- | --- | --- | --- |
| Item | Check Box |  |  |  |
| Check and overhaul the packing, bolts, fittings (and wheels if fitted) on all steel closing appliances | Annual |  |  |  |
| Check and overhaul the packing, bolts and fittings on all steel closing covers | Annual |  |  |  |
| Check that a complete set of plugs and covers (in good condition) are available for vents and openings without steel covers | Annual |  |  |  |
| Check the condition of engine room skylights if fitted | Annual |  |  |  |
| Ship side valves – overhaul | Dry-dock |  |  |  |

LSA/FFA and Loadline Maintenance Carried Out - Jan

| Date | Notes |
| --- | --- |

LSA/FFA and Loadline Maintenance Carried Out - Feb

| Date | Notes |
| --- | --- |

LSA/FFA and Loadline Maintenance Carried Out - Mar

| Date | Notes |
| --- | --- |

LSA/FFA and Loadline Maintenance Carried Out - Apr

| Date | Notes |
| --- | --- |

LSA/FFA and Loadline Maintenance Carried Out - May

| Date | Notes |
| --- | --- |

LSA/FFA and Loadline Maintenance Carried Out - Jun

| Date | Notes |
| --- | --- |

LSA/FFA and Loadline Maintenance Carried Out - Jul

| Date | Notes |
| --- | --- |

LSA/FFA and Loadline Maintenance Carried Out - Aug

| Date | Notes |
| --- | --- |

LSA/FFA and Loadline Maintenance Carried Out - Sep

| Date | Notes |
| --- | --- |

LSA/FFA and Loadline Maintenance Carried Out - Oct

| Date | Notes |
| --- | --- |

LSA/FFA and Loadline Maintenance Carried Out - Nov

| Date | Notes |
| --- | --- |

LSA/FFA and Loadline Maintenance Carried Out - Dec

| Date | Notes |
| --- | --- |

Drills

Reference shall be made to HSSEQ-03  – Schedule of Drills for various types of drills and frequency stated. Additional records to be made in the deck logbook and official logbook as applicable.

| Date | Drill | Remark |
| --- | --- | --- |

Appendix 1 - Fire Extinguisher Maintenance – General Notes

| General | Every month all fire extinguishers are to be checked for : - General condition (rust & scale, cleanliness, easy identification of type, indentations, connections & hoses, locking tags & pins, etc.) - Holding brackets remain in good condition and extinguisher safely stowed - The extinguisher is correctly identified by any nearby signs - Proper location - Confirm that there are 100% spare extinguishers or charges are available for all portable extinguishers onboard - Charging pressure (if appropriate) Every Two Years all portable extinguishers are to be serviced by an approved competent service company. Marking on an extinguisher Each extinguisher should be checked and ensure it is clearly marked with the following minimum information: - Name of the manufacturer; - Types of fire and rating for which the extinguisher is suitable; - Type and quantity of extinguishing medium; - Approval details; - Instructions for use and recharge (it is recommended that operating instructions be - Given in pictorial form, in addition to explanatory text in language understood by - The likely user); - Year of manufacture; - Temperature range over which the extinguisher will operate satisfactorily; and - Test pressure. |
| --- | --- |
| Water (soda acid) | Contents (water and pre-mix components) are to be changed every two years. |
| Water (pressurised) |  |
| Foam (pre-mix chemical) | Contents (water and pre-mix components) are to be changed every two years. |
| Foam Type (Pressurised) |  |

| Foam Type (Non-portable) |  |
| --- | --- |
| Carbon Dioxide (CO2) | Extinguisher to be weighed every month to check that the contents have not leaked out. Hydrostatic testing as per Flag regulations. |
| Dry Powder | Extinguisher is to be turned upside down every month to stop contents settling down and compacting. |
| Dry Powder (non-portable) |  |

Appendix 2 -List of IMO circulars related to LSA/FFA and Drill requirements

Vessel to refer to latest ammendment of the below circulars for aditional guidance.

| S.NO | Document Name | Dated | Catagory |
| --- | --- | --- | --- |
| 1 | MSC Cirl 1432 - REVISED GUIDELINES FOR THE MAINTENANCE ANDINSPECTION OF FIRE PROTECTION SYSTEMS AND APPLIANCES | 31-MAY-12 | FFA |
| 2 | AMENDMENTS TO THE REVISED GUIDELINES FOR THE MAINTENANCEAND INSPECTION OF FIRE PROTECTION SYSTEMS AND APPLIANCES (MSC.1/CIRC.1432) | 8-JUN-15 | FFA |
| 2 | MSC Cirl 1318 - REVISED GUIDELINES FOR THE MAINTENANCE AND INSPECTIONS OF FIXED CARBON DIOXIDE FIRE-EXTINGUISHING SYSTEMS | 25-May-21 | FFA |
| 3 | MSC Cirl 1312 - REVISED GUIDELINES FOR THE PERFORMANCE AND TESTING CRITERIA, AND SURVEYS OF FOAM CONCENTRATES FOR FIXED FIRE- EXTINGUISHING SYSTEMS | 10-Jun-09 | FFA |
| 4 | IMO Res 951 - IMPROVED GUIDELINES FOR MARINE PORTABLE FIRE EXTINGUISHERS | 25-Feb-04 | FFA |
| 5 | IMO Res A.1116(30) - ESCAPE ROUTE SIGNS AND EQUIPMENT LOCATIONMARKINGS | 5-Dec-17 | FFA |
| 6 | MSC.1/Circ.1206/Rev.1 MEASURES TO PREVENT ACCIDENTS WITHLIFEBOATS | 11-Jun-19 | DRILLS |
| 7 | MSC Cirl 1578 - GUIDELINES ON SAFETY DURING ABANDON SHIP DRILLSUSING LIFEBOATS (SUPERCEDES ANNEX 2 of MSC CIRL 1206) | 19-Jun-17 | DRILLS |
| 8 | MSC Cirl 1047 - GUIDELINES FOR MONTHLY SHIPBOARD INSPECTIONOF IMMERSION SUITS AND ANTI-EXPOSURE SUITS BY SHIPS’ CREWS | 28-May-02 | LSA |
| 9 | MSC Cirl 1114 - GUIDELINES FOR PERIODIC TESTING OF IMMERSIONSUIT AND ANTI-EXPOSURE SUIT SEAMS AND CLOSURES | 25-May-04 | LSA |
| 10 | MSC Cirl 1392 - GUIDELINES FOR EVALUATION AND REPLACEMENT OFLIFEBOAT RELEASE AND RETRIEVAL SYSTEMS | 27-May-11 | LSA |
| 11 | MSC Cirl 1584 - AMENDMENTS TO THE GUIDELINES FOR EVALUATION AND REPLACEMENT OF LIFEBOAT RELEASE AND RETRIEVAL SYSTEMS (MSC.1/CIRC.1392) | 20-Jun-17 | LSA |
| 12 | IMO Res 402 - REQUIREMENTS FOR MAINTENANCE, THOROUGH EXAMINATION, OPERATIONAL TESTING, OVERHAUL AND REPAIR OF LIFEBOATS AND RESCUE BOATS, LAUNCHING APPLIANCES AND RELEASE GEAR | 19-May-16 | LSA |
| 13 | MSC Cirl 1327 - GUIDELINES FOR THE FITTING AND USE OF FALLPREVENTER DEVICES (FPDs) | 11-Jun-09 | LSA |

CONTROLLED	Revision:15 Oct 2024