## LNG 50
LNG-50 |  |  | Form No.: LNG-50
| LNG FORCING VAPORIZERS CHECKLIST |  | Revision: 01 Date: 15 Oct 2024
Issued by: DPA Approved by: MD
| Date | Normal Ops
Time
Local Readings in Compressor Room
LNG Vaporizer | Condensate Level | 50%
| Steam shell pressure | 7 bar
| Gas Inlet Pressure | -
| Gas Outlet Pressure | 0.2 bar
| Condensate Temp. | 150- 1900C
| Flow Control Valve | Open (1 Bar)
| By-Pass Valve | 0.2 - 1.0 Bar
| Gas Outlet Temp. | -800C- 00C
| Instrument Air Pressure | -
| Steam Leakage | No leak
Forcing Vaporizer | Condensate Level | 50%
| Steam shell pressure | max 10 bar
| Gas Inlet Pressure | -
| Gas Outlet Pressure | 0.2 bar
| Condensate Temp. | 150-1900C
| Flow Control Valve | Open (1 Bar)
| By-Pass Valve | 0.2 - 1.0 Bar
| Gas Outlet Temp. | -40oC
| Instrument Air Pressure | -
| Steam Leakage | No leak
| Alarms | -
IAS readings
LNG Vaporizer | Mode | LNG or N2
| Outlet Flow SP (kg/h) | -
| Outlet Flow Mode | Auto/Man/Cas
| Outlet Temp SP (ºC) | - 40ºC
| Outlet Temp Mode | Auto/Man/Cas
| Outlet Flow (kg/h) | -
| Outlet Temp (ºC) | -800C- 00C
| Outlet Pressure (kPa) | -
| Temp. Control Valve (%) | -
| Flow Control Valve (%) | -
| Condensate Temp. (ºC) | 150- 1900C
| Steam Inlet Temp. (ºC) | -
| Vapour H. Press (kPa) | -
Forcing Vaporizer | Outlet Flow SP (kg/h) | min 1400kg/h
| Outlet Flow Mode | Auto/Man/Cas
| Outlet Temp SP (ºC) | - 40ºC
| Outlet Temp Mode | Auto/Man/Cas
| Outlet Flow (kg/h) | min 1400 kg/h
| Outlet Temp (ºC) | - 40ºC
| Outlet Pressure (kPa) | -
| Temp. Control Valve (%) | -
| Flow Control Valve (%) | -
| Condensate Temp. (ºC) | 150- 1900C
| Steam Inlet Temp. (ºC) | -
| Alarms | -
| Vapour H. Press (kPa) | -
Performing Officer's visa:
Remarks: Checklist to be done twice a day. IAS data to be cross checked with local readings.
All pressures in Bar or kPa A as mentioned, all temperatures in °C.